## Input & Results
Power Demand | Parameter | Value | Unit
| Starting Pop (N₀) | 70 | person
| Max Population (K) | 500 | person
| Pop Growth Rate ® | 50 | person/month
| Expected Ocupation (T) | 120 | month
| Site Closure (90% of T) (t_drop) | 108 | month
| Capacity Margin | 20%
Generation | Generator Sets | Value | Unit
| 200 TQG Set | 0.2 | MW
| Fuel Usage Rate | 18.375 | gph
| MEP-PU-810A/B | 0.84 | MW
| Fuel Usage Rate | 60 | gph
| Geothermal System | Value | Unit
| Mil-Loop Site Specific Output | 0.672 | MW
| Single-System Install Time | 12 | month
| Mil-Loop Installation Power Demand | 1 | MW
Site Diesel Fuel Usage | Diesel Generator Only | Value | Unit
| AverageMonthly Fuel Usage | 2530.7143 | barrels
| Total Site Fuel Usage | 303685.7143 | barrels
With Mil-Loops Installed
| AverageMonthly Fuel Usage | 1395.9643 | barrels
| Total Site Fuel Usage | 167515.7143 | barrels
| Usage Reduction | 44.84%

## Calcs-Advanced
| Demand | [6 empty] | Basic Diesel-Based Generation | [6 empty] | Demand and Generation Model with Geothermal Energy
Time (months) | Population N(t) | Capability Factor (kW/per) | Site Power Demand P(t) (MW) | Site Power Demand (MW) | Energy Demand (GWh) | Surface Footprint (m2) | Surface Footprint (acre) | Tactical Generation | Prime Generation | Deisel Generation Capacity | Tactical Fuel Usage (barrels) | Prime Fuel Usage (barrel) | Total Site Generation Capacity | Total Fuel Usage | Site Power Demand | Mil-Loop Generation Capacity | Deisel Generation Capacity | Total Site Generation Capacity | Total Fuel Usage |  | Year | Base Case Fuel Usage | Mil-Loop Installation Case Fuel Usage
1 | 120 | 1.5 | 0.18 | 0.216 | 1.1826 | 477.7704 | 0.11806 | 0.4 | 0 | 0.4 | 630 | 0 | 0.4 | 630 | 1.416 | 0 | 1.6 | 1.6 | 2520 | 1 | 1 | 14657.1429 | 33801.4286
2 | 170 | 1.5 | 0.255 | 0.306 | 1.6753 | 676.8414 | 0.16725 | 0.4 | 0 | 0.4 | 630 | 0 | 0.4 | 630 | 1.506 | 0 | 1.6 | 1.6 | 2520 | 1 | 2 | 24685.7143 | 30857.1429
3 | 220 | 1.5 | 0.33 | 0.396 | 2.1681 | 875.9124 | 0.21643 | 0.4 | 0 | 0.4 | 630 | 0 | 0.4 | 630 | 1.596 | 0 | 1.6 | 1.6 | 2520 | 1 | 3 | 31885.7143 | 29828.5714
4 | 270 | 1.5 | 0.405 | 0.486 | 2.6608 | 1074.9834 | 0.26562 | 0.6 | 0 | 0.6 | 945 | 0 | 0.6 | 945 | 1.686 | 0 | 1.8 | 1.8 | 2835 | 1 | 4 | 37028.5714 | 12342.8571
5 | 320 | 1.5 | 0.48 | 0.576 | 3.1536 | 1274.0544 | 0.31481 | 0.6 | 0 | 0.6 | 945 | 0 | 0.6 | 945 | 1.776 | 0 | 1.8 | 1.8 | 2835 | 1 | 5 | 37028.5714 | 12342.8571
6 | 370 | 1.5 | 0.555 | 0.666 | 3.6464 | 1473.1254 | 0.364 | 0.8 | 0 | 0.8 | 1260 | 0 | 0.8 | 1260 | 1.866 | 0 | 2.52 | 2.52 | 3085.7143 | 1 | 6 | 37028.5714 | 12342.8571
7 | 420 | 1.5 | 0.63 | 0.756 | 4.1391 | 1672.1964 | 0.41319 | 0.8 | 0 | 0.8 | 1260 | 0 | 0.8 | 1260 | 1.956 | 0 | 2.52 | 2.52 | 3085.7143 | 1 | 7 | 37028.5714 | 12342.8571
8 | 470 | 1.5 | 0.705 | 0.846 | 4.6319 | 1871.2674 | 0.46238 | 1 | 0 | 1 | 1575 | 0 | 1 | 1575 | 2.046 | 0 | 2.52 | 2.52 | 3085.7143 | 1 | 8 | 37028.5714 | 12342.8571
9 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 1 | 0 | 1 | 1575 | 0 | 1 | 1575 | 2.1 | 0 | 2.52 | 2.52 | 3085.7143 | 1 | 9 | 36000 | 11314.2857
10 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 1 | 0 | 1 | 1575 | 0 | 1 | 1575 | 2.1 | 0 | 2.52 | 2.52 | 3085.7143 | 1 | 10 | 11314.2857 | 0
11 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 1 | 0 | 1 | 1575 | 0 | 1 | 1575 | 2.1 | 0 | 2.52 | 2.52 | 3085.7143 | 1
12 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.1 | 0.672 | 1.68 | 2.352 | 2057.1429 | 1
13 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.1 | 0.672 | 1.68 | 2.352 | 2057.1429 | 2
14 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.1 | 0.672 | 1.68 | 2.352 | 2057.1429 | 2
15 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.1 | 0.672 | 1.68 | 2.352 | 2057.1429 | 2
16 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.1 | 0.672 | 1.68 | 2.352 | 2057.1429 | 2
17 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.1 | 0.672 | 1.68 | 2.352 | 2057.1429 | 2
18 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 0.672 | 2.52 | 3.192 | 3085.7143 | 2
19 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 0.672 | 2.52 | 3.192 | 3085.7143 | 2
20 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 0.672 | 2.52 | 3.192 | 3085.7143 | 2
21 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 0.672 | 2.52 | 3.192 | 3085.7143 | 2
22 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 0.672 | 2.52 | 3.192 | 3085.7143 | 2
23 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 0.672 | 2.52 | 3.192 | 3085.7143 | 2
24 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 1.344 | 1.68 | 3.024 | 2057.1429 | 2
25 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 1.344 | 1.68 | 3.024 | 2057.1429 | 3
26 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 1.344 | 1.68 | 3.024 | 2057.1429 | 3
27 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 1.344 | 1.68 | 3.024 | 2057.1429 | 3
28 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 1.344 | 1.68 | 3.024 | 2057.1429 | 3
29 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 1.344 | 1.68 | 3.024 | 2057.1429 | 3
30 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 3.3 | 1.344 | 2.52 | 3.864 | 3085.7143 | 3
31 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 3.3 | 1.344 | 2.52 | 3.864 | 3085.7143 | 3
32 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 3.3 | 1.344 | 2.52 | 3.864 | 3085.7143 | 3
33 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 3.3 | 1.344 | 2.52 | 3.864 | 3085.7143 | 3
34 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 3.3 | 1.344 | 2.52 | 3.864 | 3085.7143 | 3
35 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 3.3 | 1.344 | 2.52 | 3.864 | 3085.7143 | 3
36 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 3
37 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
38 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
39 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
40 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
41 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
42 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
43 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
44 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
45 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
46 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
47 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
48 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
49 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
50 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
51 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
52 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
53 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
54 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
55 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
56 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
57 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
58 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
59 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
60 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
61 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
62 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
63 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
64 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
65 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
66 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
67 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
68 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
69 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
70 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
71 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
72 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
73 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
74 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
75 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
76 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
77 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
78 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
79 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
80 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
81 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
82 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
83 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
84 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
85 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
86 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
87 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
88 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
89 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
90 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
91 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
92 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
93 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
94 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
95 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
96 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
97 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
98 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
99 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
100 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
101 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
102 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
103 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
104 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
105 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
106 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
107 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
108 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 0.9 | 2.016 | 0 | 2.016 | 0 | 9
109 | 458.3333 | 1.5 | 0.6875 | 0.825 | 4.5169 | 1824.8175 | 0.45091 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.825 | 2.016 | 0 | 2.016 | 0 | 10
110 | 416.6667 | 1.5 | 0.625 | 0.75 | 4.1063 | 1658.925 | 0.40991 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.75 | 2.016 | 0 | 2.016 | 0 | 10
111 | 375 | 1.5 | 0.5625 | 0.675 | 3.6956 | 1493.0325 | 0.36892 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.675 | 2.016 | 0 | 2.016 | 0 | 10
112 | 333.3333 | 1.5 | 0.5 | 0.6 | 3.285 | 1327.14 | 0.32793 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.6 | 2.016 | 0 | 2.016 | 0 | 10
113 | 291.6667 | 1.5 | 0.4375 | 0.525 | 2.8744 | 1161.2475 | 0.28694 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.525 | 2.016 | 0 | 2.016 | 0 | 10
114 | 250 | 1.5 | 0.375 | 0.45 | 2.4638 | 995.355 | 0.24595 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.45 | 2.016 | 0 | 2.016 | 0 | 10
115 | 208.3333 | 1.5 | 0.3125 | 0.375 | 2.0531 | 829.4625 | 0.20496 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.375 | 2.016 | 0 | 2.016 | 0 | 10
116 | 166.6667 | 1.5 | 0.25 | 0.3 | 1.6425 | 663.57 | 0.16397 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.3 | 2.016 | 0 | 2.016 | 0 | 10
117 | 125 | 1.5 | 0.1875 | 0.225 | 1.2319 | 497.6775 | 0.12297 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.225 | 2.016 | 0 | 2.016 | 0 | 10
118 | 83.3333 | 1.5 | 0.125 | 0.15 | 0.82125 | 331.785 | 0.081983 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.15 | 2.016 | 0 | 2.016 | 0 | 10
119 | 41.6667 | 1.5 | 0.0625 | 0.075 | 0.41063 | 165.8925 | 0.040991 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.075 | 2.016 | 0 | 2.016 | 0 | 10
120 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.016 | 0 | 2.016 | 0 | 10

## Test
| Demand | [6 empty] | Basic Diesel-Based Generation | [6 empty] | Demand and Generation Model with Geothermal Energy
Time (months) | Population N(t) | Capability Factor (kW/per) | Site Power Demand P(t) (MW) | Site Power Demand (MW) | Energy Demand (GWh) | Surface Footprint (m2) | Surface Footprint (acre) | Tactical Generation | Prime Generation | Deisel Generation Capacity | Tactical Fuel Usage (barrels) | Prime Fuel Usage (barrel) | Total Site Generation | Total Fuel Usage | Site Power Demand | Mil-Loop Generation Capacity | Deisel Generation Capacity | Total Site Generation | Total Fuel Usage |  | Year | Base Case Fuel Usage | Mil-Loop Installation Case Fuel Usage
1 | 120 | 1.5 | 0.18 | 0.216 | 1.1826 | 477.7704 | 0.11806 | 0.4 | 0 | 0.4 | 630 | 0 | 0.4 | 630 | 1.416 | 0 | 1.6 | 1.6 | 2520 | 1 | 1 | 14657.1429 | 33801.4286
2 | 170 | 1.5 | 0.255 | 0.306 | 1.6753 | 676.8414 | 0.16725 | 0.4 | 0 | 0.4 | 630 | 0 | 0.4 | 630 | 1.506 | 0 | 1.6 | 1.6 | 2520 | 1 | 2 | 24685.7143 | 30857.1429
3 | 220 | 1.5 | 0.33 | 0.396 | 2.1681 | 875.9124 | 0.21643 | 0.4 | 0 | 0.4 | 630 | 0 | 0.4 | 630 | 1.596 | 0 | 1.6 | 1.6 | 2520 | 1 | 3 | 31885.7143 | 29828.5714
4 | 270 | 1.5 | 0.405 | 0.486 | 2.6608 | 1074.9834 | 0.26562 | 0.6 | 0 | 0.6 | 945 | 0 | 0.6 | 945 | 1.686 | 0 | 1.8 | 1.8 | 2835 | 1 | 4 | 37028.5714 | 12342.8571
5 | 320 | 1.5 | 0.48 | 0.576 | 3.1536 | 1274.0544 | 0.31481 | 0.6 | 0 | 0.6 | 945 | 0 | 0.6 | 945 | 1.776 | 0 | 1.8 | 1.8 | 2835 | 1 | 5 | 37028.5714 | 12342.8571
6 | 370 | 1.5 | 0.555 | 0.666 | 3.6464 | 1473.1254 | 0.364 | 0.8 | 0 | 0.8 | 1260 | 0 | 0.8 | 1260 | 1.866 | 0 | 2.52 | 2.52 | 3085.7143 | 1 | 6 | 37028.5714 | 12342.8571
7 | 420 | 1.5 | 0.63 | 0.756 | 4.1391 | 1672.1964 | 0.41319 | 0.8 | 0 | 0.8 | 1260 | 0 | 0.8 | 1260 | 1.956 | 0 | 2.52 | 2.52 | 3085.7143 | 1 | 7 | 37028.5714 | 12342.8571
8 | 470 | 1.5 | 0.705 | 0.846 | 4.6319 | 1871.2674 | 0.46238 | 1 | 0 | 1 | 1575 | 0 | 1 | 1575 | 2.046 | 0 | 2.52 | 2.52 | 3085.7143 | 1 | 8 | 37028.5714 | 12342.8571
9 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 1 | 0 | 1 | 1575 | 0 | 1 | 1575 | 2.1 | 0 | 2.52 | 2.52 | 3085.7143 | 1 | 9 | 36000 | 11314.2857
10 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 1 | 0 | 1 | 1575 | 0 | 1 | 1575 | 2.1 | 0 | 2.52 | 2.52 | 3085.7143 | 1 | 10 | 11314.2857 | 0
11 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 1 | 0 | 1 | 1575 | 0 | 1 | 1575 | 2.1 | 0 | 2.52 | 2.52 | 3085.7143 | 1
12 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.1 | 0.672 | 1.68 | 2.352 | 2057.1429 | 1
13 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.1 | 0.672 | 1.68 | 2.352 | 2057.1429 | 2
14 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.1 | 0.672 | 1.68 | 2.352 | 2057.1429 | 2
15 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.1 | 0.672 | 1.68 | 2.352 | 2057.1429 | 2
16 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.1 | 0.672 | 1.68 | 2.352 | 2057.1429 | 2
17 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.1 | 0.672 | 1.68 | 2.352 | 2057.1429 | 2
18 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 0.672 | 2.52 | 3.192 | 3085.7143 | 2
19 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 0.672 | 2.52 | 3.192 | 3085.7143 | 2
20 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 0.672 | 2.52 | 3.192 | 3085.7143 | 2
21 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 0.672 | 2.52 | 3.192 | 3085.7143 | 2
22 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 0.672 | 2.52 | 3.192 | 3085.7143 | 2
23 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 0.672 | 2.52 | 3.192 | 3085.7143 | 2
24 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 1.344 | 1.68 | 3.024 | 2057.1429 | 2
25 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 1.344 | 1.68 | 3.024 | 2057.1429 | 3
26 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 1.344 | 1.68 | 3.024 | 2057.1429 | 3
27 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 1.344 | 1.68 | 3.024 | 2057.1429 | 3
28 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 1.344 | 1.68 | 3.024 | 2057.1429 | 3
29 | 500 | 2.5 | 1.25 | 1.5 | 8.2125 | 3317.85 | 0.81983 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 2.7 | 1.344 | 1.68 | 3.024 | 2057.1429 | 3
30 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 3.3 | 1.344 | 2.52 | 3.864 | 3085.7143 | 3
31 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 3.3 | 1.344 | 2.52 | 3.864 | 3085.7143 | 3
32 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 3.3 | 1.344 | 2.52 | 3.864 | 3085.7143 | 3
33 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 3.3 | 1.344 | 2.52 | 3.864 | 3085.7143 | 3
34 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 3.3 | 1.344 | 2.52 | 3.864 | 3085.7143 | 3
35 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 3.3 | 1.344 | 2.52 | 3.864 | 3085.7143 | 3
36 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 3
37 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
38 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
39 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
40 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
41 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
42 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
43 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
44 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
45 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
46 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
47 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
48 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 4
49 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
50 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
51 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
52 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
53 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
54 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
55 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
56 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
57 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
58 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
59 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
60 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 5
61 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
62 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
63 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
64 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
65 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
66 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
67 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
68 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
69 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
70 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
71 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
72 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 6
73 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
74 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
75 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
76 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
77 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
78 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
79 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
80 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
81 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
82 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
83 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
84 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 7
85 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
86 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
87 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
88 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
89 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
90 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
91 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
92 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
93 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
94 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
95 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
96 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 8
97 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
98 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
99 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
100 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
101 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
102 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
103 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
104 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
105 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
106 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
107 | 500 | 3.5 | 1.75 | 2.1 | 11.4975 | 4644.99 | 1.1478 | 0 | 2.52 | 2.52 | 0 | 3085.7143 | 2.52 | 3085.7143 | 2.1 | 2.016 | 0.84 | 2.856 | 1028.5714 | 9
108 | 500 | 1.5 | 0.75 | 0.9 | 4.9275 | 1990.71 | 0.4919 | 0 | 1.68 | 1.68 | 0 | 2057.1429 | 1.68 | 2057.1429 | 0.9 | 2.016 | 0 | 2.016 | 0 | 9
109 | 458.3333 | 1.5 | 0.6875 | 0.825 | 4.5169 | 1824.8175 | 0.45091 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.825 | 2.016 | 0 | 2.016 | 0 | 10
110 | 416.6667 | 1.5 | 0.625 | 0.75 | 4.1063 | 1658.925 | 0.40991 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.75 | 2.016 | 0 | 2.016 | 0 | 10
111 | 375 | 1.5 | 0.5625 | 0.675 | 3.6956 | 1493.0325 | 0.36892 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.675 | 2.016 | 0 | 2.016 | 0 | 10
112 | 333.3333 | 1.5 | 0.5 | 0.6 | 3.285 | 1327.14 | 0.32793 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.6 | 2.016 | 0 | 2.016 | 0 | 10
113 | 291.6667 | 1.5 | 0.4375 | 0.525 | 2.8744 | 1161.2475 | 0.28694 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.525 | 2.016 | 0 | 2.016 | 0 | 10
114 | 250 | 1.5 | 0.375 | 0.45 | 2.4638 | 995.355 | 0.24595 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.45 | 2.016 | 0 | 2.016 | 0 | 10
115 | 208.3333 | 1.5 | 0.3125 | 0.375 | 2.0531 | 829.4625 | 0.20496 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.375 | 2.016 | 0 | 2.016 | 0 | 10
116 | 166.6667 | 1.5 | 0.25 | 0.3 | 1.6425 | 663.57 | 0.16397 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.3 | 2.016 | 0 | 2.016 | 0 | 10
117 | 125 | 1.5 | 0.1875 | 0.225 | 1.2319 | 497.6775 | 0.12297 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.225 | 2.016 | 0 | 2.016 | 0 | 10
118 | 83.3333 | 1.5 | 0.125 | 0.15 | 0.82125 | 331.785 | 0.081983 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.15 | 2.016 | 0 | 2.016 | 0 | 10
119 | 41.6667 | 1.5 | 0.0625 | 0.075 | 0.41063 | 165.8925 | 0.040991 | 0 | 0.84 | 0.84 | 0 | 1028.5714 | 0.84 | 1028.5714 | 0.075 | 2.016 | 0 | 2.016 | 0 | 10
120 | 0 | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.016 | 0 | 2.016 | 0 | 10